## Slide 1: Presenter’s name Title and Affiliation
Presenter’s Bio

## Slide 2: Optimal coordination of directional earth fault overcurrent relays 67N in interconnected electric power systems
Date
P. M. De Oliveira-De Jesus1, E. Sorrentino2, J. S. Abello1, O. Archilla1 C. A. Alza1, D. Celeita1, G. A. Ramos1, A. J. Urdaneta3
1 Universidad de los Andes, Bogotá, Colombia
2 Universidad Carlos III, Madrid, Spain.
3 Universidad Simón Bolívar, Caracas, Venezuela

## Slide 3: Table of Contents
Introduction/Backgroud
Proposed Approach
Case Study
Assumptions
Results
Findings

## Slide 4: Introduction/Background
Fact 1: Coordination of Directional Overcurrent Relays (DOCR) in Interconnected Systems is still a Challenging problem.
Why? For the fault in 1-2
Primary-Backup pairs are:
2-4, 4-6, 6-8, 8-2 1-7, 7-5, 5-3, 3-1
Defining Time Delayed Settings of of pairs 3-1 and 8-2 are confli- cting because TDS1 and TDS2 were already specified in 1-7 and 2-4.

## Slide 5: Introduction/Background
Fact 2: Optimization is a suitable way to solve the coordination of DOCR problem seeking maximum operation speed and full selectivity. Since 1988 nearly 450 contributions have been published in this topic focused only in the 67P (phase) function [1].
[1]
Fact 3: There are no contributions in Literature about optimal coordination of 67N function (phase-to-ground faults)

## Slide 6: Introduction/Background
Fact 4: Evidence of renewed interest in DOCR optimization under the smartgrid/microgrid paradigm at distribution level. Why? Directional overcurrent 67P/67N function is a cost-effective alternative for weakly meshed distribution networks.
Fact 5: High-impedance phase-to-ground faults are very common in distribution systems.
what is the gap?
  No contributions about Optimal Coordination of 67N overcurrent relays
  We do not know how a high-impedance fault affects speed and selectivity of the protection system adjusted via optimization

## Slide 7: Introduction/Background
To fulfill the research gap we investigate the impact of high-impedance single-phase to neutral/earth faults in the optimal clearing times and selectivity of the protection system when the relay settings of the 67N function are determined using a optimization procedure.

## Slide 8: Proposed Approach
To fulfill the research gap we investigate the impact of high-impedance single-phase to neutral/earth faults in the optimal clearing times and selectivity of the protection system when the relay settings of the 67N function are determined using a optimization procedure.
Selectivity criteria of relays I and j
for near-end/far fault h at line k
Protection model basics:
Primary relay must trip first!

## Slide 9
Proposed Approach
The optimization model is linear and it was taken from [1]
The idea is finding the set of all time dial settings D such that:
Minimize Operation Time
Maximize Speed
Assure Full selectivity. [Primary relay must trip first!]
According to relay delay lower and upper bounds

## Slide 10: Proposed Approach
Phase-ground shortcircuit current calculations required to
setup the optimization model are determined using the EPRI’s
OpenDSS solver and the Neutral-Earth Model (Multi-phase/
Multigrounded model).
We do not use the sequence approach.
Thus calculated short-circuit currents seen by the relays
account:
The correct fault current distribution across the earth/neutral path including the effect of grounding resistances.
The effect of high-impedance faults upon current distributions

## Slide 11: Proposed Approach
Method: The short circuit program and optimization model is run several times varying the fault resistance (RF) from 0 (solid) to 50 ohms in steps of 0.1 ohm.
The output variables are:
Objective Function: Overall Operation Time in seconds as a function of RF
Optimal Time Dial Settings as a function of RF

## Slide 12: Case Study
We convert the well-known 69kV positive-sequence three-bus system included in [1] into a multiphase/multigrouded system:
Both systems are equivalent,
with the same positive-sequence
impedances

## Slide 13: Case Study
We convert the 69kV positive-sequence three-bus system
included in [1] into a multiphase/multigrouded
System using realistic data

## Slide 14: Case Study
Assumptions:
The fault impedance is the same for all the faulted lines in each step.
All asymmetrical phase-to-neutral faults were located at same phase a.
Transient configurations are not included.
Load currents are neglected
The sensitivity problem is previously solved (all pickup sett. are 50A).
Short-circuit current magnitudes are assumed as invariant
Only time-delayed relays are considered.
Circuit breaker operation times are not included in the model.
IEC standard curves are considered, and all the relays are assumed to be with the same curve (Standard Inverse).
Resistance of all ground mats at substations are equal to zero.
Grounding resistances at towers are set as 5 ohms.
The optimization model is built considering that near-end and far-end Faults occur at substations.
Influence of stability constraints is not considered.

## Slide 15: Case Study
General structure of the optimization model for the 3-bus case study:
This problem was solved with Matlab’s LinProg tool
with fault currents taken from the OpenDSS engine
using the COM interface.

## Slide 16: Results
Case 1 – Solid Fault RF=0 ohm.
The solution for RF =0 is OF= 3.6551s. The resulting optimal time dial settings are
D1 =0.2711, D2 =0.2427, D3 =0.2579, D4 =0.2703, D5 =0.2387, D6 =0.2553

## Slide 17: Results
Case 2 – Solid Fault RF=10 ohm.
The solution for RF =10 is OF= 2.3222s. The resulting optimal time dial settings are
D1 =0.1617, D2 =0.1282, D3 =0.1457, D4 =0.1572, D5 =0.1247, D6 =0.1484
Faster
Than
Case 1!
TDSs are lower Than Case 1!

## Slide 18: Results
Solid Fault ranging from RF=0 ohms to RF = 50 ohms.
Faster operation
Operation time
Deteriorates as far as
RF grows and fault
currents decrease
With RF > 15-20 ohms
Some TDS are bounded to the minimum!

## Slide 19: Results
Solid Fault ranging from RF=0 ohms to RF = 50 ohms.
With RF > 25 ohms
All TDS are bounded to the minimum!

## Slide 20: Verification
Verifying the quality of the solution for
Case 1 (RF=0) ohms and Case 2 (RF = 10) ohms.
Case 1
Case 2
In both cases, after 5000 simulated (random location) faults, the protection system accomplish in all the cases the coordination criteria: tback-tmain > C = 200ms

## Slide 21: Findings
In this work we analyzed how optimal operation times and selectivity regarded to optimal coordination of neutral directional overcurrent relays are affected considering different impedance phase-to-neutral fault magnitudes.
Usually optimal coordination is made assuming solid faults. The optimal procedure is carried in a wide range of fault impedances from 0 (solid fault) to high-impedance faults where the sensitivity is lost and the optimization problem becomes not well-defined.
Results show how the optimal operation time decreases and the selectivity is guaranteed as far as the fault impedance magnitude increases. In this process the calculated time dial settings also decrease stagnating at their minimum values. Beyond this point, the time dials stuck and the clearing times deteriorate as far the fault impedance also increases

## Slide 22: Findings
We also find that if the TDSs are specified for solid faults and the actual fault type is non-solid, simulations show a non-optimal solution (larger operation times) but accomplishing the selectivity criteria assuming no transient configurations during the tripping interval. This means that current practice based on the use of solid faults is suboptimal from operation speed viewpoint.
The main limitation of this work lies on the deterministic representation of the fault resistance. Future work must pose this problem as a stochastic optimization problem.
Future research would be devoted to solve this problem considering a more realistic condition accounting transient configurations during the clearing time process. In this case, the use of near-end and far-end faults o setup the optimization model should not be enough to assure full selectivity.